## SFPE Metric
SFPE Calculations - Ref: Human Behavior in Fire, June 2003, Society of Fire Protection Engineers
Constants:
| This software is provided as is, and no claim is made as to the the accuracy or suitability of this software. The user takes full and exclusive responsibility for using this software. Please report any errors to support@thunderheadeng.com |  |  |  |  | a = | 0.266 | 1/a= | 3.7594
[6 empty] | dens_cutoff = | 0.55
| Color Code: | Input | Output |  | This data is used in speed calculations
|  | Speed: |  |  |  | Egress Component | k (m/s)
|  | Density: | 1.82 | pers/m^2 (no reduction if dens < 0.55) |  | Corridor, Door | 1.4
|  | Egress Component | Corridor, Door | Select type in the pulldown menu |  | Stair (190/254) | 1
[6 empty] | Stair (178/279) | 1.08 | Note: SFPE manual has an error in this label
|  | k use = | 1.4 |  |  | Stair (165/305) | 1.16
|  | SFPE Speed = | 0.72223 | m/s |  | Stair (165/330) | 1.23
|  | Flow Calculated Using User Input Density: |  |  | This data is used in flow rate calculations
|  | Width = | 2.4 | m
|  | Egress Component | Corridors |  |  | Component | Layer (m)
[6 empty] | Chairs, Benches | 0
|  | Boundary Layer = | 0.2 | m |  | Handrails | 0.089
|  | Specific Flow = | 1.3145 | pers/s-m |  | Obstacles | 0.1
|  | Flow Rate = | 2.6289 | pers/s |  | Stairways, Doors | 0.15
|  |  | 157.7355 | pers/min |  | Corridors | 0.2
|  | Max Flow Using Max Specific Flow Density (1.88 pers/m^2): |  |  | Speed Chart
|  | SFPE Speed at 1.88 pers/m^2= | 0.7 | m/s |  | Dens | Corridor | Stair (190/254) | Stair (272/279) | Stair (165/305) | Stair (165/330)
|  | Max Specific Flow = | 1.3158 | pers/s-m
|  | Max Flow Rate = | 2.6316 | pers/s |  | 0 | 1.19 | 0.85 | 0.918 | 0.986 | 1.0455
|  |  | 157.8947 | pers/min |  | 0.55 | 1.19 | 0.85 | 0.918 | 0.986 | 1.0455
[6 empty] | 3.7594 | 0 | 0 | 0 | 0 | 0
[6 empty] | 4 | 0 | 0 | 0 | 0 | 0
Specific Flow Chart
[6 empty] | Dens | Corridor | Stair (190/254) | Stair (272/279) | Stair (165/305) | Stair (165/330)
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0.075188 | 0.089474 | 0.06391 | 0.069023 | 0.074135 | 0.078609
[6 empty] | 0.15038 | 0.17895 | 0.12782 | 0.13805 | 0.14827 | 0.15722
[6 empty] | 0.22556 | 0.26842 | 0.19173 | 0.20707 | 0.22241 | 0.23583
[6 empty] | 0.30075 | 0.35789 | 0.25564 | 0.27609 | 0.29654 | 0.31444
[6 empty] | 0.37594 | 0.44737 | 0.31955 | 0.34511 | 0.37068 | 0.39305
[6 empty] | 0.45113 | 0.53684 | 0.38346 | 0.41414 | 0.44481 | 0.47165
[6 empty] | 0.52632 | 0.62632 | 0.44737 | 0.48316 | 0.51895 | 0.55026
[6 empty] | 0.6015 | 0.70737 | 0.50526 | 0.54568 | 0.58611 | 0.62147
[6 empty] | 0.67669 | 0.77684 | 0.55489 | 0.59928 | 0.64367 | 0.68251
[6 empty] | 0.75188 | 0.84211 | 0.6015 | 0.64962 | 0.69774 | 0.73985
[6 empty] | 0.82707 | 0.90316 | 0.64511 | 0.69672 | 0.74833 | 0.79349
[6 empty] | 0.90226 | 0.96 | 0.68571 | 0.74057 | 0.79543 | 0.84343
[6 empty] | 0.97744 | 1.0126 | 0.72331 | 0.78117 | 0.83904 | 0.88967
[6 empty] | 1.0526 | 1.0611 | 0.75789 | 0.81853 | 0.87916 | 0.93221
[6 empty] | 1.1278 | 1.1053 | 0.78947 | 0.85263 | 0.91579 | 0.97105
[6 empty] | 1.203 | 1.1453 | 0.81805 | 0.88349 | 0.94893 | 1.0062
[6 empty] | 1.2782 | 1.1811 | 0.84361 | 0.9111 | 0.97859 | 1.0376
[6 empty] | 1.3534 | 1.2126 | 0.86617 | 0.93546 | 1.0048 | 1.0654
[6 empty] | 1.4286 | 1.24 | 0.88571 | 0.95657 | 1.0274 | 1.0894
[6 empty] | 1.5038 | 1.2632 | 0.90226 | 0.97444 | 1.0466 | 1.1098
[6 empty] | 1.5789 | 1.2821 | 0.91579 | 0.98905 | 1.0623 | 1.1264
[6 empty] | 1.6541 | 1.2968 | 0.92632 | 1.0004 | 1.0745 | 1.1394
[6 empty] | 1.7293 | 1.3074 | 0.93383 | 1.0085 | 1.0832 | 1.1486
[6 empty] | 1.8045 | 1.3137 | 0.93835 | 1.0134 | 1.0885 | 1.1542
[6 empty] | 1.8797 | 1.3158 | 0.93985 | 1.015 | 1.0902 | 1.156
[6 empty] | 1.9549 | 1.3137 | 0.93835 | 1.0134 | 1.0885 | 1.1542
[6 empty] | 2.0301 | 1.3074 | 0.93383 | 1.0085 | 1.0832 | 1.1486
[6 empty] | 2.1053 | 1.2968 | 0.92632 | 1.0004 | 1.0745 | 1.1394
[6 empty] | 2.1805 | 1.2821 | 0.91579 | 0.98905 | 1.0623 | 1.1264
[6 empty] | 2.2556 | 1.2632 | 0.90226 | 0.97444 | 1.0466 | 1.1098
[6 empty] | 2.3308 | 1.24 | 0.88571 | 0.95657 | 1.0274 | 1.0894
[6 empty] | 2.406 | 1.2126 | 0.86617 | 0.93546 | 1.0048 | 1.0654
[6 empty] | 2.4812 | 1.1811 | 0.84361 | 0.9111 | 0.97859 | 1.0376
[6 empty] | 2.5564 | 1.1453 | 0.81805 | 0.88349 | 0.94893 | 1.0062
[6 empty] | 2.6316 | 1.1053 | 0.78947 | 0.85263 | 0.91579 | 0.97105
[6 empty] | 2.7068 | 1.0611 | 0.75789 | 0.81853 | 0.87916 | 0.93221
[6 empty] | 2.782 | 1.0126 | 0.72331 | 0.78117 | 0.83904 | 0.88967
[6 empty] | 2.8571 | 0.96 | 0.68571 | 0.74057 | 0.79543 | 0.84343
[6 empty] | 2.9323 | 0.90316 | 0.64511 | 0.69672 | 0.74833 | 0.79349
[6 empty] | 3.0075 | 0.84211 | 0.6015 | 0.64962 | 0.69774 | 0.73985
[6 empty] | 3.0827 | 0.77684 | 0.55489 | 0.59928 | 0.64367 | 0.68251
[6 empty] | 3.1579 | 0.70737 | 0.50526 | 0.54568 | 0.58611 | 0.62147
[6 empty] | 3.2331 | 0.63368 | 0.45263 | 0.48884 | 0.52505 | 0.55674
[6 empty] | 3.3083 | 0.55579 | 0.39699 | 0.42875 | 0.46051 | 0.4883
[6 empty] | 3.3835 | 0.47368 | 0.33835 | 0.36541 | 0.39248 | 0.41617
[6 empty] | 3.4586 | 0.38737 | 0.27669 | 0.29883 | 0.32096 | 0.34033
[6 empty] | 3.5338 | 0.29684 | 0.21203 | 0.22899 | 0.24595 | 0.2608
[6 empty] | 3.609 | 0.20211 | 0.14436 | 0.15591 | 0.16746 | 0.17756
[6 empty] | 3.6842 | 0.10316 | 0.073684 | 0.079579 | 0.085474 | 0.090632
[6 empty] | 3.7594 | -5.8433e-15 | -4.1738e-15 | -4.5077e-15 | -4.8416e-15 | -5.1337e-15

## SFPE English
SFPE Calculations - Ref: Human Behavior in Fire, June 2003, Society of Fire Protection Engineers
Constants:
| This software is provided as is, and no claim is made as to the the accuracy or suitability of this software. The user takes full and exclusive responsibility for using this software. Please report any errors to support@thunderheadeng.com |  |  |  |  | a = | 2.86 | 1/a= | 0.34965
[6 empty] | dens cutoff = | 0.051
This data is used in speed calculations
| Color Code: | Input | Output
[6 empty] | Egress Component | k (ft/min)
|  | Speed: |  |  |  | Corridor, Door | 275
|  | Density: | 0.169 | pers/ft^2 (no reduction if dens < 0.051) |  | Stair (7.5/10) | 196
|  | Egress Component | Stair (7.0/11) | Select type in the pulldown menu |  | Stair (7.0/11) | 212
[6 empty] | Stair (6.5/12) | 229
|  | k use = | 212 |  |  | Stair (6.5/13) | 242
|  | SFPE Speed = | 109.5319 | ft/min
This data is used in flow rate calculations
Flow Calculated Using User Input Density:
|  | Width = | 72 | in |  | Component | Layer (in)
|  | Egress Component | Stairways, Doors |  |  | Chairs, Benches | 0
[6 empty] | Handrails | 3.5
|  | Boundary Layer = | 6 | in |  | Obstacles | 4
|  | Specific Flow = | 18.5109 | pers/min-ft |  | Stairways, Doors | 6
|  | Flow Rate = | 92.5545 | pers/min |  | Corridors | 8
|  |  | 1.5426 | pers/s
Speed Chart:
|  | Max Flow Using Max Specific Flow Density (0.1748 pers/ft^2): |  |  |  | Dens | Corridor | Stair (7.5/10) | Stair (7.0/11) | Stair (6.5/12) | Stair (6.5/13)
|  | SFPE Speed at 0.1748 pers/ft^2= | 106 | ft/min
|  | Max Specific Flow = | 18.5315 | pers/min-ft |  | 0 | 233.75 | 166.6 | 180.2 | 194.65 | 205.7
|  | Max Flow Rate = | 92.6573 | pers/min |  | 0.051 | 233.75 | 166.6 | 180.2 | 194.65 | 205.7
|  |  | 1.5443 | pers/s |  | 0.34965 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0.4 | 0 | 0 | 0 | 0 | 0
Specific Flow Chart:
[6 empty] | Dens | Corridor | Stair (7.5/10) | Stair (7.0/11) | Stair (6.5/12) | Stair (6.5/13)
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0.006993 | 1.6346 | 1.165 | 1.2601 | 1.3612 | 1.4385
[6 empty] | 0.013986 | 3.2692 | 2.3301 | 2.5203 | 2.7224 | 2.8769
[6 empty] | 0.020979 | 4.9038 | 3.4951 | 3.7804 | 4.0836 | 4.3154
[6 empty] | 0.027972 | 6.5385 | 4.6601 | 5.0406 | 5.4448 | 5.7538
[6 empty] | 0.034965 | 8.1731 | 5.8252 | 6.3007 | 6.8059 | 7.1923
[6 empty] | 0.041958 | 9.8077 | 6.9902 | 7.5608 | 8.1671 | 8.6308
[6 empty] | 0.048951 | 11.4423 | 8.1552 | 8.821 | 9.5283 | 10.0692
[6 empty] | 0.055944 | 12.9231 | 9.2106 | 9.9625 | 10.7614 | 11.3723
[6 empty] | 0.062937 | 14.1923 | 10.1152 | 10.941 | 11.8183 | 12.4892
[6 empty] | 0.06993 | 15.3846 | 10.965 | 11.8601 | 12.8112 | 13.5385
[6 empty] | 0.076923 | 16.5 | 11.76 | 12.72 | 13.74 | 14.52
[6 empty] | 0.083916 | 17.5385 | 12.5001 | 13.5206 | 14.6048 | 15.4338
[6 empty] | 0.090909 | 18.5 | 13.1855 | 14.2618 | 15.4055 | 16.28
[6 empty] | 0.097902 | 19.3846 | 13.8159 | 14.9438 | 16.1421 | 17.0585
[6 empty] | 0.1049 | 20.1923 | 14.3916 | 15.5664 | 16.8147 | 17.7692
[6 empty] | 0.11189 | 20.9231 | 14.9124 | 16.1298 | 17.4232 | 18.4123
[6 empty] | 0.11888 | 21.5769 | 15.3785 | 16.6338 | 17.9677 | 18.9877
[6 empty] | 0.12587 | 22.1538 | 15.7897 | 17.0786 | 18.4481 | 19.4954
[6 empty] | 0.13287 | 22.6538 | 16.146 | 17.4641 | 18.8645 | 19.9354
[6 empty] | 0.13986 | 23.0769 | 16.4476 | 17.7902 | 19.2168 | 20.3077
[6 empty] | 0.14685 | 23.4231 | 16.6943 | 18.0571 | 19.505 | 20.6123
[6 empty] | 0.15385 | 23.6923 | 16.8862 | 18.2646 | 19.7292 | 20.8492
[6 empty] | 0.16084 | 23.8846 | 17.0232 | 18.4129 | 19.8894 | 21.0185
[6 empty] | 0.16783 | 24 | 17.1055 | 18.5018 | 19.9855 | 21.12
[6 empty] | 0.17483 | 24.0385 | 17.1329 | 18.5315 | 20.0175 | 21.1538
[6 empty] | 0.18182 | 24 | 17.1055 | 18.5018 | 19.9855 | 21.12
[6 empty] | 0.18881 | 23.8846 | 17.0232 | 18.4129 | 19.8894 | 21.0185
[6 empty] | 0.1958 | 23.6923 | 16.8862 | 18.2646 | 19.7292 | 20.8492
[6 empty] | 0.2028 | 23.4231 | 16.6943 | 18.0571 | 19.505 | 20.6123
[6 empty] | 0.20979 | 23.0769 | 16.4476 | 17.7902 | 19.2168 | 20.3077
[6 empty] | 0.21678 | 22.6538 | 16.146 | 17.4641 | 18.8645 | 19.9354
[6 empty] | 0.22378 | 22.1538 | 15.7897 | 17.0786 | 18.4481 | 19.4954
[6 empty] | 0.23077 | 21.5769 | 15.3785 | 16.6338 | 17.9677 | 18.9877
[6 empty] | 0.23776 | 20.9231 | 14.9124 | 16.1298 | 17.4232 | 18.4123
[6 empty] | 0.24476 | 20.1923 | 14.3916 | 15.5664 | 16.8147 | 17.7692
[6 empty] | 0.25175 | 19.3846 | 13.8159 | 14.9438 | 16.1421 | 17.0585
[6 empty] | 0.25874 | 18.5 | 13.1855 | 14.2618 | 15.4055 | 16.28
[6 empty] | 0.26573 | 17.5385 | 12.5001 | 13.5206 | 14.6048 | 15.4338
[6 empty] | 0.27273 | 16.5 | 11.76 | 12.72 | 13.74 | 14.52
[6 empty] | 0.27972 | 15.3846 | 10.965 | 11.8601 | 12.8112 | 13.5385
[6 empty] | 0.28671 | 14.1923 | 10.1152 | 10.941 | 11.8183 | 12.4892
[6 empty] | 0.29371 | 12.9231 | 9.2106 | 9.9625 | 10.7614 | 11.3723
[6 empty] | 0.3007 | 11.5769 | 8.2512 | 8.9248 | 9.6404 | 10.1877
[6 empty] | 0.30769 | 10.1538 | 7.2369 | 7.8277 | 8.4554 | 8.9354
[6 empty] | 0.31469 | 8.6538 | 6.1678 | 6.6713 | 7.2063 | 7.6154
[6 empty] | 0.32168 | 7.0769 | 5.0439 | 5.4557 | 5.8931 | 6.2277
[6 empty] | 0.32867 | 5.4231 | 3.8652 | 4.1807 | 4.5159 | 4.7723
[6 empty] | 0.33566 | 3.6923 | 2.6316 | 2.8464 | 3.0747 | 3.2492
[6 empty] | 0.34266 | 1.8846 | 1.3432 | 1.4529 | 1.5694 | 1.6585
[6 empty] | 0.34965 | 0 | 0 | 0 | 0 | 0

## Equations
SFPE Calculations - Ref: Human Behavior in Fire, June 2003, Society of Fire Protection Engineers