## Sheet1
NFPA 130 and SFPE evacuation calculations. Follow NFPA 130 approach.
Table C.1.3 Sample Calculations |  |  |  | Single Entity Flow Rate
|  | NFPA 130 | SFPE | Egress Component | NFPA 130 | SFPE
|  | (p/min) | (p/min)
| Platform to concourse (downward) |  |  | Stairs and Escalators (7x11) | p/min | p/min
| Stairs (4) | 406 | 370.4 | Stairs 1830 mm (72 in.) | 101.5 | 92.6
| Escalators (2 - one discounted) | 68 | 55.6 | Escalators 1220 mm (48 in.) | 67.5 | 55.6
| Emergency stairs (2) | 135 | 111.2 | Stairs 1220 mm (48 in.) | 67.5 | 55.6
| Total Flow Rate | 609 | 537.2
|  |  |  | Doors | p/min | p/min
| Through fare barriers |  |  | Fare gate 530 mm (21 in.) | 50 | 18
| Fare gates (4) | 200 | 72 | Service gate 1220 mm (48 in.) | 60 | 72.1
| Service gate (1) | 60 | 72.1 | Emergency exit door 1830 mm (72 in.) | 150 | 120.2
| Emergency exit doors (2) | 300 | 240.4
| Total Flow Rate | 560 | 384.5 | Walking Speed | m/min (ft/min) | m/min (ft/min)
|  |  |  | Speed at density of 1.82 p/m2 (0.17 p/ft2) | 37.7 (124) | 43.4 (142)
Walking time
| T1 On platform (136 ft) | 1.09 | 0.95775
| T2 Platform to concourse | 0.62 | 0.53908
| T3 On concourse (54 ft) | 0.44 | 0.38028
| Concourse to grade | 0 | 0
| Grade to safe (10 ft) | 0.08 | 0.070423
| Total Time | 2.23 | 1.9475
| Fp (time to clear platform, 2314 occupants) | 3.7997 | 4.3075
| Wp (waiting at platform exits) | 2.7097 | 3.3498
| Fp*Emergency stair capacity | 512.9557 | 478.9963
| Concourse occupant load | 1801.0443 | 1835.0037
| Ffb (fare barrier flow time) | 3.2162 | 4.7724
| Wfb (waiting at fare barriers) | 0 | 0.46492
| Wc (waiting at concourse exits) | 0 | 0
| T (walking time) | 2.23 | 1.9475
| Total time (min) = | 4.9397 | 5.7622
| Total time (s) = | 296.3803 | 345.7338